## MAU
MAKE-UP AIR HANDLING UNIT SCHEDULE
UNIT MARK | LOCATION | SERVICE | M3/HR | ESP(Pa) | FAN |  |  |  |  | COOLING COIL-1 | [11 empty] | HEATING COIL-1 | [11 empty] | Front WASH PUMP |  |  |  | COOLING COIL-2 | [11 empty] | HEATING COIL-1 | [11 empty] | MOTOR |  |  |  | WASH PUMP |  |  |  | FILTER EFF% |  |  | ENERGY-SAVING RECTIFIER DIFFUSER |  |  |  | REMARK
[5 empty] | TYPE | DRIVE TYPE | TSP(Pa) | RPM | EFFICIENCY % | FACE VEL M/S MAX. | ROWS/FP | CAP (KW) | EAT ℃ |  | LAT ℃ |  | AIR△P Pa | L/S | EWT | LWT | WTR△P Kpa | FACE VEL M/S MAX. | ROWS/FP | CAP (KW) | EAT ℃ |  | LAT ℃ |  | AIR△P Pa | L/S | EWT | LWT | WTR△P Kpa | QTY | HEAD(M) | POWER(KW) | VOLTAGE | FACE VEL M/S MAX. | ROWS/FP | CAP (KW) | EAT ℃ |  | LAT ℃ |  | AIR△P Pa | L/S | EWT | LWT | WTR△P Kpa | FACE VEL M/S MAX. | ROWS/FP | CAP (KW) | EAT ℃ |  | LAT ℃ |  | AIR△P Pa | L/S | EWT | LWT | WTR△P Kpa | ABSORBED POWER (KW) | POWER (KW) | VOLTAGE | TYPE | QTY | HEAD(M) | POWER(KW) | VOLTAGE | PRE-FILTER | FINAL | HEPA @0.3um | MATERIAL | FRAME | BLADE | REMARKS
[13 empty] | DB | WB | DB | WB |  |  | ℃ | ℃ |  |  |  |  | DB | WB | DB | WB |  |  | ℃ | ℃ | [8 empty] | DB | WB | DB | WB |  |  | ℃ | ℃ |  |  |  |  | DB | WB | DB | WB |  |  | ℃ | ℃
F2-CRMAU-101 | S-FAB L10 | CLEAN ROOM | 120000 | 700 | BACKWARD INCLINED | DIRECT | - | - | - | 2.5 | - | 2234 | 35 | 31.8 | 18 | 17.8 | - | 66.7 | 12 | 20 | <50 | 2.5 | - | 742 | 5 | 1.4 | 23 | 10.4 | - | 29.5 | 35 | 29 | <50 | 1 | 35 | 4 | 3/480/60 | 2.5 | - | 880 | 18 | 17.8 | 9.7 | 9.5 | - | 26.3 | 5 | 13 | <50 | 2.5 | - | 504 | 9.7 | 9.5 | 22 | 14.6 | - | 20.1 | 35 | 29 | <50 | - | 132 | 3/460/60 | TEFC | 1 | 45 | 7.5 | 3/480/60 |  | 95 | 99.97 | SUS-304 | 2.5mmt | 1.5mmt | Double-Side Welding of Flange | IE4, CLASS MOTOR, W/VARIABLE FREQUENCY DRIVE, FILTER SELECTIO IS QUALIFIED TO MEET MERV 13,需含2道化學濾網(濾筒型), 預留1道化學濾網空間
F2-CRMAU-102 | S-FAB L10 | CLEAN ROOM | 120000 | 700 | BACKWARD INCLINED | DIRECT | - | - | - | 2.5 | - | 2234 | 35 | 31.8 | 18 | 17.8 | - | 66.7 | 12 | 20 | <50 | 2.5 | - | 742 | 5 | 1.4 | 23 | 10.4 | - | 29.5 | 35 | 29 | <50 | 1 | 35 | 4 | 3/480/60 | 2.5 | - | 880 | 18 | 17.8 | 9.7 | 9.5 | - | 26.3 | 5 | 13 | <50 | 2.5 | - | 504 | 9.7 | 9.5 | 22 | 14.6 | - | 20.1 | 35 | 29 | <50 | - | 132 | 3/460/60 | TEFC | 1 | 45 | 7.5 | 3/480/60 |  | 95 | 99.97 | SUS-304 | 2.5mmt | 1.5mmt | Double-Side Welding of Flange | IE4, CLASS MOTOR, W/VARIABLE FREQUENCY DRIVE, FILTER SELECTIO IS QUALIFIED TO MEET MERV 13,需含2道化學濾網(濾筒型), 預留1道化學濾網空間
F2-CRMAU-103 | S-FAB L10 | CLEAN ROOM | 120000 | 700 | BACKWARD INCLINED | DIRECT | - | - | - | 2.5 | - | 2234 | 35 | 31.8 | 18 | 17.8 | - | 66.7 | 12 | 20 | <50 | 2.5 | - | 742 | 5 | 1.4 | 23 | 10.4 | - | 29.5 | 35 | 29 | <50 | 1 | 35 | 4 | 3/480/60 | 2.5 | - | 880 | 18 | 17.8 | 9.7 | 9.5 | - | 26.3 | 5 | 13 | <50 | 2.5 | - | 504 | 9.7 | 9.5 | 22 | 14.6 | - | 20.1 | 35 | 29 | <50 | - | 132 | 3/460/60 | TEFC | 1 | 45 | 7.5 | 3/480/60 |  | 95 | 99.97 | SUS-304 | 2.5mmt | 1.5mmt | Double-Side Welding of Flange | IE4, CLASS MOTOR, W/VARIABLE FREQUENCY DRIVE, FILTER SELECTIO IS QUALIFIED TO MEET MERV 13,需含2道化學濾網(濾筒型), 預留1道化學濾網空間
F2-CRMAU-104 | S-FAB L10 | CLEAN ROOM | 120000 | 700 | BACKWARD INCLINED | DIRECT | - | - | - | 2.5 | - | 2234 | 35 | 31.8 | 18 | 17.8 | - | 66.7 | 12 | 20 | <50 | 2.5 | - | 742 | 5 | 1.4 | 23 | 10.4 | - | 29.5 | 35 | 29 | <50 | 1 | 35 | 4 | 3/480/60 | 2.5 | - | 880 | 18 | 17.8 | 9.7 | 9.5 | - | 26.3 | 5 | 13 | <50 | 2.5 | - | 504 | 9.7 | 9.5 | 22 | 14.6 | - | 20.1 | 35 | 29 | <50 | - | 132 | 3/460/60 | TEFC | 1 | 45 | 7.5 | 3/480/60 |  | 95 | 99.97 | SUS-304 | 2.5mmt | 1.5mmt | Double-Side Welding of Flange | IE4, CLASS MOTOR, W/VARIABLE FREQUENCY DRIVE, FILTER SELECTIO IS QUALIFIED TO MEET MERV 13,需含2道化學濾網(濾筒型), 預留1道化學濾網空間
F2-CRMAU-105 | S-FAB L10 | CLEAN ROOM | 120000 | 700 | BACKWARD INCLINED | DIRECT | - | - | - | 2.5 | - | 2234 | 35 | 31.8 | 18 | 17.8 | - | 66.7 | 12 | 20 | <50 | 2.5 | - | 742 | 5 | 1.4 | 23 | 10.4 | - | 29.5 | 35 | 29 | <50 | 1 | 35 | 4 | 3/480/60 | 2.5 | - | 880 | 18 | 17.8 | 9.7 | 9.5 | - | 26.3 | 5 | 13 | <50 | 2.5 | - | 504 | 9.7 | 9.5 | 22 | 14.6 | - | 20.1 | 35 | 29 | <50 | - | 132 | 3/460/60 | TEFC | 1 | 45 | 7.5 | 3/480/60 |  | 95 | 99.97 | SUS-304 | 2.5mmt | 1.5mmt | Double-Side Welding of Flange | IE4, CLASS MOTOR, W/VARIABLE FREQUENCY DRIVE, FILTER SELECTIO IS QUALIFIED TO MEET MERV 13,需含2道化學濾網(濾筒型), 預留1道化學濾網空間
F2-CRMAU-106 | S-FAB L10 | CLEAN ROOM | 120000 | 700 | BACKWARD INCLINED | DIRECT | - | - | - | 2.5 | - | 2234 | 35 | 31.8 | 18 | 17.8 | - | 66.7 | 12 | 20 | <50 | 2.5 | - | 742 | 5 | 1.4 | 23 | 10.4 | - | 29.5 | 35 | 29 | <50 | 1 | 35 | 4 | 3/480/60 | 2.5 | - | 880 | 18 | 17.8 | 9.7 | 9.5 | - | 26.3 | 5 | 13 | <50 | 2.5 | - | 504 | 9.7 | 9.5 | 22 | 14.6 | - | 20.1 | 35 | 29 | <50 | - | 132 | 3/460/60 | TEFC | 1 | 45 | 7.5 | 3/480/60 |  | 95 | 99.97 | SUS-304 | 2.5mmt | 1.5mmt | Double-Side Welding of Flange | IE4, CLASS MOTOR, W/VARIABLE FREQUENCY DRIVE, FILTER SELECTIO IS QUALIFIED TO MEET MERV 13,需含2道化學濾網(濾筒型), 預留1道化學濾網空間
F2-CRMAU-107 | S-FAB L10 | CLEAN ROOM | 120000 | 700 | BACKWARD INCLINED | DIRECT | - | - | - | 2.5 | - | 2234 | 35 | 31.8 | 18 | 17.8 | - | 66.7 | 12 | 20 | <50 | 2.5 | - | 742 | 5 | 1.4 | 23 | 10.4 | - | 29.5 | 35 | 29 | <50 | 1 | 35 | 4 | 3/480/60 | 2.5 | - | 880 | 18 | 17.8 | 9.7 | 9.5 | - | 26.3 | 5 | 13 | <50 | 2.5 | - | 504 | 9.7 | 9.5 | 22 | 14.6 | - | 20.1 | 35 | 29 | <50 | - | 132 | 3/460/60 | TEFC | 1 | 45 | 7.5 | 3/480/60 |  | 95 | 99.97 | SUS-304 | 2.5mmt | 1.5mmt | Double-Side Welding of Flange | IE4, CLASS MOTOR, W/VARIABLE FREQUENCY DRIVE, FILTER SELECTIO IS QUALIFIED TO MEET MERV 13,需含2道化學濾網(濾筒型), 預留1道化學濾網空間
F2-CRMAU-108 | S-FAB L10 | CLEAN ROOM | 120000 | 700 | BACKWARD INCLINED | DIRECT | - | - | - | 2.5 | - | 2234 | 35 | 31.8 | 18 | 17.8 | - | 66.7 | 12 | 20 | <50 | 2.5 | - | 742 | 5 | 1.4 | 23 | 10.4 | - | 29.5 | 35 | 29 | <50 | 1 | 35 | 4 | 3/480/60 | 2.5 | - | 880 | 18 | 17.8 | 9.7 | 9.5 | - | 26.3 | 5 | 13 | <50 | 2.5 | - | 504 | 9.7 | 9.5 | 22 | 14.6 | - | 20.1 | 35 | 29 | <50 | - | 132 | 3/460/60 | TEFC | 1 | 45 | 7.5 | 3/480/60 |  | 95 | 99.97 | SUS-304 | 2.5mmt | 1.5mmt | Double-Side Welding of Flange | IE4, CLASS MOTOR, W/VARIABLE FREQUENCY DRIVE, FILTER SELECTIO IS QUALIFIED TO MEET MERV 13,需含2道化學濾網(濾筒型), 預留1道化學濾網空間
F2-CRMAU-109 | S-FAB L10 | CLEAN ROOM | 120000 | 700 | BACKWARD INCLINED | DIRECT | - | - | - | 2.5 | - | 2234 | 35 | 31.8 | 18 | 17.8 | - | 66.7 | 12 | 20 | <50 | 2.5 | - | 742 | 5 | 1.4 | 23 | 10.4 | - | 29.5 | 35 | 29 | <50 | 1 | 35 | 4 | 3/480/60 | 2.5 | - | 880 | 18 | 17.8 | 9.7 | 9.5 | - | 26.3 | 5 | 13 | <50 | 2.5 | - | 504 | 9.7 | 9.5 | 22 | 14.6 | - | 20.1 | 35 | 29 | <50 | - | 132 | 3/460/60 | TEFC | 1 | 45 | 7.5 | 3/480/60 |  | 95 | 99.97 | SUS-304 | 2.5mmt | 1.5mmt | Double-Side Welding of Flange | IE4, CLASS MOTOR, W/VARIABLE FREQUENCY DRIVE, FILTER SELECTIO IS QUALIFIED TO MEET MERV 13,需含2道化學濾網(濾筒型), 預留1道化學濾網空間,STANDBY
F2-CRMAU-110 | S-FAB L10 | CLEAN ROOM | 120000 | 700 | BACKWARD INCLINED | DIRECT | - | - | - | 2.5 | - | 2234 | 35 | 31.8 | 18 | 17.8 | - | 66.7 | 12 | 20 | <50 | 2.5 | - | 742 | 5 | 1.4 | 23 | 10.4 | - | 29.5 | 35 | 29 | <50 | 1 | 35 | 4 | 3/480/60 | 2.5 | - | 880 | 18 | 17.8 | 9.7 | 9.5 | - | 26.3 | 5 | 13 | <50 | 2.5 | - | 504 | 9.7 | 9.5 | 22 | 14.6 | - | 20.1 | 35 | 29 | <50 | - | 132 | 3/460/60 | TEFC | 1 | 45 | 7.5 | 3/480/60 |  | 95 | 99.97 | SUS-304 | 2.5mmt | 1.5mmt | Double-Side Welding of Flange | IE4, CLASS MOTOR, W/VARIABLE FREQUENCY DRIVE, FILTER SELECTIO IS QUALIFIED TO MEET MERV 13,需含2道化學濾網(濾筒型), 預留1道化學濾網空間, Future
MAKE-UP AIR HANDLING UNIT SCHEDULE
UNIT MARK | LOCATION | SERVICE | QTY | FAN |  |  |  | COOLING COIL-1 | [8 empty] | HEATING COIL
|  |  |  | TYPE | CMH | ESP(Pa) | RPM | FACE VEL M/S MAX. | CAP (KW) | EAT ℃ |  | LAT ℃ |  | EWT | LWT | L/S | FACE VEL M/S MAX. | CAP (KW) | EAT ℃ |  | LAT ℃ |  | EWT | LWT | L/S | REMARK
[10 empty] | DB | WB | DB | WB | ℃ | ℃ |  |  |  | DB | WB | DB | WB | ℃ | ℃
MMTN-F2-MAU-AH101 | N-FAB L10~L20 | GAS ROOM & ELECTRICITY ROOM | 1 | BACKWARD CURVED | 100000 | 500 | - | 2.5 | 1650 | 35 | 31.8 | 19.2 | 19 | 5 | 13 | 55.1 | 2.5 | 606 | 5 | 14 | 23 | 10.4 | 35 | 29 | 24.1
MMTN-F2-MAU-AH102 | N-FAB L10~L20 | GAS ROOM & ELECTRICITY ROOM | 1 | BACKWARD CURVED | 100000 | 500 | - | 2.5 | 1650 | 35 | 31.8 | 19.2 | 19 | 5 | 13 | 55.1 | 2.5 | 606 | 5 | 14 | 23 | 10.4 | 35 | 29 | 24.1
MMTN-F2-MAU-AH103 | N-FAB L10~L40 | OFFICE L10~L40 | 1 | BACKWARD CURVED | 40000 | 700 | - | 2.5 | 740 | 35 | 31.8 | 19.2 | 19 | 5 | 13 | 22.1 | - | - | - | - | - | - | - | - | -
MMTN-F2-MAU-AH104 | N-FAB L10~L40 | OFFICE L10~L40 | 1 | BACKWARD CURVED | 40000 | 700 | - | 2.5 | 740 | 35 | 31.8 | 19.2 | 19 | 5 | 13 | 22.1 | - | - | - | - | - | - | - | - | -