## CT 規格
COOLING TOWER CELL SCHEDULE
UNIT MARK | L/S | EMT ℃ | LMT ℃ | AIR TEMP ℃WB | MOTOR |  |  | TYPE | REMARK
[5 empty] | HP | VOLTAGE | TYPE
F1-C3-CT-006 | 514 | 38.4 | 32.4 | 29.4 | 95.2 | 3/460/60 | TEFC | COUNTERFLOW | W/VFD,IE4
F1-C3-CT-007 | 514 | 38.4 | 32.4 | 29.4 | 95.2 | 3/460/60 | TEFC | COUNTERFLOW | W/VFD,IE4
F1-C3-CT-008 | 514 | 38.4 | 32.4 | 29.4 | 95.2 | 3/460/60 | TEFC | COUNTERFLOW | W/VFD,IE4
F1-C3-CT-009 | 514 | 38.4 | 32.4 | 29.4 | 95.2 | 3/460/60 | TEFC | COUNTERFLOW | W/VFD,IE4
F1-C3-CT-010 | 514 | 38.4 | 32.4 | 29.4 | 95.2 | 3/460/60 | TEFC | COUNTERFLOW | W/VFD,IE4 | Future
COOLING TOWER FILTRATION SYSTEM
UNIT MARK | SERVICE | FILTRATION TANK |  |  | DESIGN PRESSURE | FILTER |  | FILTRATION PUMP
|  | QTY | MATERIAL | MATERIAL DIMENSION DxH(mm) | KPA | TYPE | EFF. | UNIT MARK | L/S | TYPE | HEAD m | MOTOR |  |  | REMARK
[12 empty] | KW | VOLTAGE | TYPE
F1-C3-FS-R104 | CONDENSER WATER FILTRATION | 1 | CARBON STEEL | ⊕2438 x 2881 | 350 | SAND | 90%@5um | F1-C3-FSP-R106 | 63.5 | IN-LINE | 24.4 | 22 | 3/460/60 | TEFC | IE4
F1-C3-FS-R105 | CONDENSER WATER FILTRATION | 1 | CARBON STEEL | ⊕2438 x 2881 | 350 | SAND | 90%@5um | F1-C3-FSP-R106 | 63.5 | IN-LINE | 24.4 | 22 | 3/460/60 | TEFC | IE4 | STANDBY