## Pump 規格
HVAC PUMP SCHEDULE
UNIT MARK | SERVICE | TYPE | SUCTION SIZE A | DISCHARGE SIZE A | FLOW L/S | HEAD M | BHP | RPM | MOTOR |  |  | FLUID | REMARK
[9 empty] | HP | VOLTAGE | TYPE
F1-C3-12CHP-007 | CHILLED WATER PRODUCTION | IN-LINE | 300 | 300 | 288 | 44 | - | - | 250 | 3/460/60 | TEFC | WATER | W/VFD,IE4
F1-C3-12CHP-008 | CHILLED WATER PRODUCTION | IN-LINE | 300 | 300 | 288 | 44 | - | - | 250 | 3/460/60 | TEFC | WATER | W/VFD,IE4
F1-C3-12CHP-009 | CHILLED WATER PRODUCTION | IN-LINE | 300 | 300 | 288 | 44 | - | - | 250 | 3/460/60 | TEFC | WATER | W/VFD,IE4
F1-C3-12CHP-010 | CHILLED WATER PRODUCTION | IN-LINE | 300 | 300 | 288 | 44 | - | - | 250 | 3/460/60 | TEFC | WATER | W/VFD,IE4
F1-C3-12CHP-011 | CHILLED WATER PRODUCTION | IN-LINE | 300 | 300 | 288 | 44 | - | - | 250 | 3/460/60 | TEFC | WATER | W/VFD,IE4 | STANDBY
F1-C3-12CHP-012 | CHILLED WATER PRODUCTION | IN-LINE | 300 | 300 | 288 | 44 | - | - | 250 | 3/460/60 | TEFC | WATER | W/VFD,IE4 | Future
F1-C3-12CHP-013 | CHILLED WATER PRODUCTION | IN-LINE | 300 | 300 | 288 | 44 | - | - | 250 | 3/460/60 | TEFC | WATER | W/VFD,IE4 | Future
F1-C3-12CHP-014 | CHILLED WATER PRODUCTION | IN-LINE | 300 | 300 | 288 | 44 | - | - | 250 | 3/460/60 | TEFC | WATER | W/VFD,IE4 | Future
F1-C3-12CWP-007 | CONDENSER WTAER | IN-LINE | 350 | 350 | 356 | 28 | - | - | 200 | 3/460/60 | TEFC | WATER | W/VFD,IE4
F1-C3-12CWP-008 | CONDENSER WTAER | IN-LINE | 350 | 350 | 356 | 28 | - | - | 200 | 3/460/60 | TEFC | WATER | W/VFD,IE4
F1-C3-12CWP-009 | CONDENSER WTAER | IN-LINE | 350 | 350 | 356 | 28 | - | - | 200 | 3/460/60 | TEFC | WATER | W/VFD,IE4
F1-C3-12CWP-010 | CONDENSER WTAER | IN-LINE | 350 | 350 | 356 | 28 | - | - | 200 | 3/460/60 | TEFC | WATER | W/VFD,IE4
F1-C3-12CWP-011 | CONDENSER WTAER | IN-LINE | 350 | 350 | 356 | 28 | - | - | 200 | 3/460/60 | TEFC | WATER | W/VFD,IE4 | STANDBY
F1-C3-12CWP-012 | CONDENSER WTAER | IN-LINE | 350 | 350 | 356 | 28 | - | - | 200 | 3/460/60 | TEFC | WATER | W/VFD,IE4 | Future
F1-C3-12CWP-013 | CONDENSER WTAER | IN-LINE | 350 | 350 | 356 | 28 | - | - | 200 | 3/460/60 | TEFC | WATER | W/VFD,IE4 | Future
F1-C3-12CWP-014 | CONDENSER WTAER | IN-LINE | 350 | 350 | 356 | 28 | - | - | 200 | 3/460/60 | TEFC | WATER | W/VFD,IE4 | Future
F1-C3-35WWP-001 | 35℃ WARM WATER | IN-LINE | 300 | 300 | 200 | 44 | - | - | 175 | 3/460/60 | TEFC | WATER | W/VFD,IE4
F1-C3-35WWP-002 | 35℃ WARM WATER | IN-LINE | 300 | 300 | 200 | 44 | - | - | 175 | 3/460/60 | TEFC | WATER | W/VFD,IE4
F1-C3-35WWP-003 | 35℃ WARM WATER | IN-LINE | 300 | 300 | 200 | 44 | - | - | 175 | 3/460/60 | TEFC | WATER | W/VFD,IE4
F1-C3-35WWP-004 | 35℃ WARM WATER | IN-LINE | 300 | 300 | 200 | 44 | - | - | 175 | 3/460/60 | TEFC | WATER | W/VFD,IE4
F1-C3-35WWP-005 | 35℃ WARM WATER | IN-LINE | 300 | 300 | 200 | 44 | - | - | 175 | 3/460/60 | TEFC | WATER | W/VFD,IE4 | Future
F1-C3-CDA-CHWP-001 | CUB3 CDA COOLING WATER | IN-LINE | 125 | 125 | 55 | 25 | - | - | 30 | 3/460/60 | TEFC | WATER | W/VFD,IE4
F1-C3-CDA-CHWP-002 | CUB3 CDA COOLING WATER | IN-LINE | 125 | 125 | 55 | 25 | - | - | 30 | 3/460/60 | TEFC | WATER | W/VFD,IE4 | STANDBY
PCW PUMP SCHEDULE
UNIT MARK | LOCATION | SERVICE | TYPE | FLOW RATE m3/h | HEAD m | MATERIAL |  |  | SUCTION NOZZLE | DISCHARGE NOZZLE |  | EFFICIENCY % | MOTOR
[6 empty] | VOLUTE CASING | CASING COVER | IMPELLER |  |  |  |  | KW | VOLTAGE | TYPE | REMARK
FAL-PCW-P-101 | S-FAB L20 | L20 15.5℃ SYSTEM | HORIZONTAL, END-SUCTION PUMP | 800 | 85 | STAINLESS STEEL 1.4408 | STAINLESS STEEL 1.4408 | STAINLESS STEEL 1.4408 | DN350 | DN350 |  | 80 | 222 | 3/480/60 | TEFC | MOTOR W/VFD & IE4
FAL-PCW-P-102 | S-FAB L20 | L20 15.5℃ SYSTEM | HORIZONTAL, END-SUCTION PUMP | 800 | 85 | STAINLESS STEEL 1.4408 | STAINLESS STEEL 1.4408 | STAINLESS STEEL 1.4408 | DN350 | DN350 |  | 80 | 222 | 3/480/60 | TEFC | MOTOR W/VFD & IE4
FAL-PCW-P-103 | S-FAB L20 | L20 15.5℃ SYSTEM | HORIZONTAL, END-SUCTION PUMP | 800 | 85 | STAINLESS STEEL 1.4408 | STAINLESS STEEL 1.4408 | STAINLESS STEEL 1.4408 | DN350 | DN350 |  | 80 | 222 | 3/480/60 | TEFC | MOTOR W/VFD & IE4
FAL-PCW-P-104 | S-FAB L20 | L20 15.5℃ SYSTEM | HORIZONTAL, END-SUCTION PUMP | 800 | 85 | STAINLESS STEEL 1.4408 | STAINLESS STEEL 1.4408 | STAINLESS STEEL 1.4408 | DN350 | DN350 |  | 80 | 222 | 3/480/60 | TEFC | MOTOR W/VFD & IE4
FAL-PCW-P-105 | S-FAB L20 | L20 15.5℃ SYSTEM | HORIZONTAL, END-SUCTION PUMP | 800 | 85 | STAINLESS STEEL 1.4408 | STAINLESS STEEL 1.4408 | STAINLESS STEEL 1.4408 | DN350 | DN350 |  | 80 | 222 | 3/480/60 | TEFC | MOTOR W/VFD & IE4
FAL-PCW-P-106 | S-FAB L20 | L20 15.5℃ SYSTEM | HORIZONTAL, END-SUCTION PUMP | 800 | 85 | STAINLESS STEEL 1.4408 | STAINLESS STEEL 1.4408 | STAINLESS STEEL 1.4408 | DN350 | DN350 |  | 80 | 222 | 3/480/60 | TEFC | MOTOR W/VFD & IE4 (STANDBY)
FAL-PCW-P-107 | S-FAB L20 | L20 15.5℃ SYSTEM | HORIZONTAL, END-SUCTION PUMP | 800 | 85 | STAINLESS STEEL 1.4408 | STAINLESS STEEL 1.4408 | STAINLESS STEEL 1.4408 | DN350 | DN350 |  | 80 | 222 | 3/480/60 | TEFC | MOTOR W/VFD & IE4 (Future)